## Sayfa2
LULEBURGAZ CHAMBER OF COMMERCE AND INDUSTRY
LULEBURGAZ CHAMBER OF COMMERCE TRAINING CENTRE CONSTRUCTION WORK ELECTRICAL SPECIFICATIONS
APPLICABLE STANDARDS
The standards and regulations specified below shall apply to the implementation of the installations specified in the project and to the equipment to be used. In case of insufficiency, international standards shall be consulted for information. Where necessary, the interpretation of the relevant specifications or standards shall be carried out by the administration and control engineering.
a- Standards:
Special Technical Specifications and Unit Price Schedule.
Ministry of Environment and Urbanisation Regulations.
Electrical Installation Regulations.
Regulations on High Voltage Electrical Installations.
Regulations on Earthing in Electrical Installations.
TEDAŞ Electricity Energy Facilities Project Regulation.
High-voltage installations with a commemorative current exceeding 1KV
General Technical Specifications for Electricity Distribution Facilities.
Electrical Installations Acceptance Regulations.
Electrical Installation Safety Regulations.
TSE Lightning Protection Regulation.
EMO High Structures Regulation.
EMO Joint Antenna TV/R and Cable TV/R Distribution Internal Installation Regulations.
Elevator Regulation dated 15 February 2003 and numbered 25021 (95/16 EC)
Turkish Telecommunications Inc. Technical Specifications for In-Building Telephone Installations and Telephone Network Installation Regulations
IEC, VDE, DIN, BS, NEC Standards
Serial No. | 1 | Serial No.
Item No. | 35.450.2600
Description | TWINAXIAL 2x1.5mm² CABLE
Unit | MT
Specification | Cables of international quality, consisting of a pair of live and shielded copper wires for balanced audio signal transmission, including all small parts and labour. Note: Payment shall be made under B.F.T. 35.500.2000 and related items.
Serial No. | 2
Item No. | 35.450.2700
Description | MULTICORE AUDIO CABLE
Unit | MT
Specification | Delivery of a multicore audio cable assembly consisting of 8 numbered cables for carrying audio signals, including all small materials and labour. Note: Payment shall be made from B.F.T. 35.500.2000 and related items.
Serial No. | 4
Item No. | 35.450.1002
Description | 16-channel Audio Mixer
Unit | AD
Specification | The device used for sound broadcasting and control shall be equipped with a high-input capacity stereo equaliser channel appropriate for the number of channels, featuring mono stereo inputs, Aux outputs, fader-equipped outputs for recording purposes, and a digital effects-equipped operator sound control mixer. The supply shall include an automatic voltage-selecting switch for the sound mixer, delivered in working condition, including all small parts and labour. Intermediate values will be determined by interpolation.
Serial No. | E-1
Item No. | 35.450.5003
Description | HANDHELD MICROPHONE
Unit | AD
Specification | A crystal or dynamic microphone compliant with TS 6509 standard and with the specifications stated in the technical specifications, a microphone cable at least 10 m long, a microphone socket and plug, installation in place, all small materials and labour included, delivery in working condition.
Serial No. | E-2
Item No. | 35.470.3003
Description | 300X225 MOTORISED CURTAIN
Unit
Specification | Curtain in 4:3 format, front projection type, curtain image gain at least 1.2, curtain viewing angle at least 150°, motorised and remotely controllable, with M1 7201-96 fire protection certification, curtain and motor protection made of aluminium material enclosure, delivery of the motorised screen including all minor materials and labour. Intermediate values will be determined by interpolation.
Serial No. | E-3
Item No. | 35.450.1407
Description | 3x10 w column-type speaker
Unit | AD
Specification | Supply of loudspeakers and loudspeaker enclosures in accordance with TS 976 EN 60268-5 standard, with the specifications stated in the technical specifications, including installation, all small materials and labour, and delivery in working order.
Serial No. | E-4
Item No. | 35.430.1310
Description | Ceiling Speaker
Unit | AD
Specification | The loudspeaker must be transformer-driven and capable of being driven at 6W, 3W, 1.5W and 0.75W. The support box to be attached to the rear of the loudspeaker must protect the loudspeaker from dust and dripping water from above. The ceiling loudspeaker shall be placed on the market with the CE conformity mark, in accordance with the TS EN 54-24 standard. The loudspeaker must have a ceramic screw terminal block, thermal fuse and heat-resistant high-temperature connection. The maximum power must be at least 9W. (nominal 6/3/1.5/0.75) The sound pressure level at 6W power must be at least 90 dB and the manufacturer must clearly state this on the product information page. The speaker must be manufactured in accordance with the TS EN 54-24 standard and the 305/2011/EU Construction Products Regulation, and placed on the market with the CE conformity mark. It must be accompanied by the manufacturer's performance declaration and a Certificate of Performance Constancy issued by an organisation accredited by the European Union. The delivery, installation, and testing of ceiling speakers, including all small materials, must be carried out at the workplace, and they must be delivered in working order.
Serial No. | E-5
Item No. | 35.550.1006
Description | Rack cabinets 12u 600 mm * 600 mm 19"
Unit | AD
Specification | Certified by an accredited testing organisation as compliant with the TS EN 61587-1 standard, the carrier inner uprights (2 at the front and 2 at the rear) are of a bent structure with a minimum thickness of 1.5 mm. The side panels of the cabinets are made of DKP sheet metal with a minimum thickness of 1 mm. with 19" wide upright spacing, the bottom chassis of the cabinets has a cable entry section that prevents dust ingress and has the ability to secure cables, the front and side covers of the cabinets are lockable with a key, removable, the front covers of the cabinets are tamper-proof, anti-static, secure, fume-coloured, with a rod-mounted glass panel at least 4 mm thick, at least 135 degrees, key-locked, openable, removable, with a frame structure around the glass panel at least 3 cm wide, held in place by screws and metal fasteners to increase the strength of the front panel glass, painted with electrostatic powder paint, with ventilation grilles on the top and/or side surfaces of the cabinets, square holes on the cabinet uprights with each side measuring at least 9.5±0.01 mm, cabinet uprights that can move along the depth of the cabinets, and the cabinet installed in working order, including all small mounting materials.
Serial No. | E-6
Item No. | 35.450.5706
Description | 300 watt amplifier
Unit | AD
Specification | An audio amplifier with the specifications stated in the technical specifications, including its mounting on the iron frame at the designated location, its frame, paintwork, all small materials and labour, delivered in working order.
Serial No. | 7
Item No. | 35.505.2030
Description | U/UTP Cat6 copper data cable
Unit | MT
Specification | For horizontal installations in local area networks (LAN), 4-pair, 4-colour-coded (blue-blue white, orange-orange white, green-green white, brown -brown white) unshielded twisted pairs, all enclosed in a PVC outer jacket around a star-shaped separator, 4-pair cable, Cat 6 Standard, 23 AWG (American Wire Gauge) 0.57 mm bare copper cladding, ANSI/TIA/EIA-568, TS EN 50288-5-1, ISO 11801 standards, delivery to the workplace, all small materials, labour, installation, testing included (if passed through a pipe, the pipe cost is paid from the relevant budget; if passed through a cable tray, the channel cost is paid from the relevant budget).
Serial No. | E-11
Item No. | 35.445.1302
Description | En az 4 MP İç Ortam Dome Kamera
Unit | ADET
Specification | Yüksek Çözünürlüklü, Renkli, S/B, Gece/Gündüz Fonksiyonlu Dome tipi IP Kamera. En az 1/3'' CMOS sensöre sahip, 2MP çözünürlük değerini en az 25 fps (resim/sn)/30 fps (resim/sn), 4 MP çözünürlük değerini en az 20 fps (resim/sn) olarak desteklemelidir. Kamera mekanik IR kesici filtreli olmalı, gerçek (true) Day/Night özelliğe sahip olmalıdır. Kamera görüş açısı 3,2 mm ile 9 mm arasında ayarlanabilen motorize lense sahip olmalıdır. Kamera otomatik backfokus (auto focus, remote focus) özelliğine sahip olmalıdır. Kamera H.265, H.264 ve MJPEG görüntü sıkıştırma formatlarını desteklemelidir. Kamera en az 120 dB WDR (Geniş Dinamik Işık Aralığı), ROI, 3D-DNR, BLC, özelliklerini desteklemelidir. Kamera TS EN 60529 standardına göre en az IP66 koruma ve TS EN 62262 standardına göre en az IK10 mekanik dayanım derecelerine sahip olmalıdır. 12 Volt DC harici besleme girişi olmalıdır. Elektromanyetik Uyumluluk Yönetmeliği'ne ve TS EN55032, TS EN55024, TS EN 50130-4 standartlarına uygun olarak CE işareti ile piyasaya arz edilmiş kameranın iş yerine nakli, montajı, her nevi ufak montaj malzemeleri dahil işler halde teslimi.
Serial No. | E-12
Item No. | 35.445.1502
Description | 16-Channel (Network Video Recorder)
Unit | AD
Specification | The device must support 8MP recording and allow for the simultaneous live viewing of at least 16 2MP cameras. The recording device must support H.265, H.264, and MJPEG formats. The device must have an input bandwidth of at least 160 Mbps. The device must have a 10/100 Mbit Ethernet port. The device must have a high-resolution HDMI output. The device must have at least one VGA screen output. The device must have at least two hard disk drives. The device shall have a hard disk with a minimum storage capacity of 12 TB. The device shall be placed on the market with the CE conformity mark in accordance with the 2014/35/EU Directive on electrical equipment designed for specific voltage limits, including transportation to the workplace, installation, and delivery in working order, including all minor installation materials.
Serial No. | E-13
Item No. | KTB.ELK-20.001
Description | 22-inch CONTROL PANEL LCD CCTV MONITOR
Unit | AD
Specification | Technical Specifications and Manufacturing Conditions: 1) Monitors must be video monitors manufactured for security purposes, suitable for 24-hour operation, and not intended for use with TVs or PCs. 2) They must be LCD monitors with a minimum size of 20‘ and a maximum size of 22’, suitable for desktop use. 3) They shall have a minimum service life of 30,000 hours. 4) Brightness value shall be min 200 cd/m², contrast ratio min 1000:1. 5) They shall support a minimum resolution of 1920x1080. 6) Response time must be a maximum of 5ms. 7) Video input: 1 x VGA, 1 x HDMI. 8) Supplied with a desk stand. 9) Dot pitch must be a maximum of 0.25 x 0.25mm. 10) The monitor must meet and be certified to the standards listed below. Safety Certificate: EN60950, CE Electromagnetic Emission Standard: EN55022 class B, FCC part 15 class B Environmental Electromagnetic Immunity: EN50130-4 (CE) The price quoted is for the supply, delivery to the workplace, installation, and all general expenses, including the contractor's profit, for one unit of the product with the technical specifications stated above, delivered in working order.
Serial No. | 8
Item No. | 35.160.3331
Description | Normal sortie
Unit | AD
Specification | Line and sorting lines made of lead-free antigron (NHXMH) material
Serial No. | 9
Item No. | 35.160.3332
Description | Commutator sortie
Unit | AD
Specification | Line and sorting lines made of lead-free antigron (NHXMH) material
Serial No. | 10
Item No. | 35.160.3334
Description | Parallel sortie
Unit | AD
Specification | Linye ve sorti hatları kurşunsuz antigron (NHXMH) nevinden malzeme ile
Serial No. | 11
Item No. | 35.185.1101
Description | recessed standard key
Unit | AD
Specification | A standard switch with a body and cover made of non-flammable material, with contacts and screw terminals that can withstand at least 250 V and 6 A, in accordance with TS EN 60669-1, including supply, transportation to the workplace, and installation of the case, including any minor materials and labor.
Serial No. | 12
Item No. | 35.185.1102
Description | flush-mounted switch
Unit | AD
Specification | A standard switch with a non-flammable body and cover, equipped with contacts and screw terminals capable of withstanding at least 250 V and 6 A.e in accordance with TS EN 60669-1, including supply, delivery to the workplace, and installation on site, including all small materials and labour.
Serial No. | E-20
Item No. | 35.440.2104
Description | 3-hour dual-sided emergency directional luminaire (LED) that illuminates during power failure
Unit | AD
Specification | Colour and marking formats compliant with relevant standards, single or double-sided, LED light source, compliant with TS EN 60598-2 -22 standard and the Regulation on the Control of Waste Electrical and Electronic Equipment, the Regulation on the Protection of Buildings against Fire, the 2014/35/EU Regulation on Electrical Equipment Designed for Specific Voltage Limits, and TS ISO 3864-1/2, TS ISO 7010, TS EN 1838, TS EN 60598-1, and TS EN 50172 standards, and placed on the market with the CE conformity mark.
Serial No. | E-25
Item No. | 35.170.2142
Description | Recessed ceiling luminaire with LED, minimum dimensions 30x30 (light output at least 1000 lm, luminaire luminous efficacy at least 100 lm/w)
Unit | MT
Specification | All LED luminaires shall be ENEC certified or TSE product certified or possess a product certificate issued by an accredited certification body, and the driver shall have a PFC value of at least 0.95. The LEDs used shall be IESNA LM-80 certified. The service life of the luminaires shall be at least 50,000 (L70) hours according to the TM-21 calculation table, the colour rendering index (CRI) of the luminaires shall be at least 80, and they shall have a homogeneous light distribution. The luminaires shall comply with the TS EN 60598-1, TS 8698 EN 60598-2-1, TS EN 60598-2-2 standards, the luminaire drivers shall comply with the TS EN 61347-1 and TS EN 61347-2-13 standards, and shall be placed on the market with the CE conformity mark in accordance with the Regulation on Electrical Equipment Designed for Specific Voltage Limits. Regulation on Electrical Equipment Designed for Specific Voltage Limits. The luminaires shall have a photometric measurement report in accordance with IESNA LM-79 standards obtained from an accredited laboratory, IP protection rating tests shall be performed in accordance with TS 3033 EN 60529 standard, and protection rating tests for IK values shall be performed in accordance with TS EN 62262 standard. Furthermore, the luminaires shall be manufactured in compliance with the Regulation on the Control of Waste Electrical and Electronic Equipment. Note: The luminous flux (lm) values specified for LED luminaire positions are the output values of the luminaire, while the power consumption indicates the total power drawn by the luminaire from the mains. Supply of luminaires with a body made of at least 0.5 mm thick DKP sheet metal, a frame made of at least 0.7 mm thick DKP sheet metal, an opal PMMA diffuser with a minimum thickness of 1 mm, and a minimum IP 40 protection rating, delivered to the workplace in working order, including all materials, labour, and installation.
Serial No. | E-26
Item No. | 35.170.2140
Description | Recessed, LED circular (downlight) luminaire (light output at least 800 lm, luminaire luminous efficacy at least 100 lm/w).
Unit | MT
Specification | All LED luminaires shall be ENEC certified or TSE product certified or possess a product certificate issued by an accredited certification body, and the driver shall have a PFC value of at least 0.95. The LEDs used shall be IESNA LM-80 certified. The service life of the luminaires shall be at least 50,000 (L70) hours according to the TM-21 calculation table, the colour rendering index (CRI) of the luminaires shall be at least 80, and they shall have a homogeneous light distribution. The luminaires shall comply with TS EN 60598-1, TS 8698 EN 60598-2-1, TS EN 60598-2-2 standards, the luminaire drivers shall comply with TS EN 61347-1 and TS EN 61347-2-13 standards, and shall be placed on the market with the CE conformity mark in accordance with the Regulation on Electrical Equipment Designed for Specific Voltage Limits. Regulation on Electrical Equipment Designed for Specific Voltage Limits. The luminaires shall have a photometric measurement report in accordance with IESNA LM-79 standards obtained from an accredited laboratory, IP protection rating tests shall be performed in accordance with TS 3033 EN 60529 standard, and protection rating tests for IK values shall be performed in accordance with TS EN 62262 standard. Furthermore, the luminaires shall be manufactured in compliance with the Regulation on the Control of Waste Electrical and Electronic Equipment. Note: The luminous flux (lm) values specified for LED luminaire positions are the output values of the luminaire, while the power consumption indicates the total power drawn by the luminaire from the mains. Supply of luminaires with an aluminium cast body and cooling section, opal PMMA diffuser, and a minimum IP 40 protection rating to the workplace, including all materials, labour, and installation, delivered in working order.
Serial No. | 14,15,16,17,18
Item No. | 35.160.3503
Description | Line and branch circuits with lead-free antigron (NHXMH) material for standard socket sorties
Unit | AD
Specification | Installation of sockets with external covers and safety features using fully waterproof materials (plugs, connectors, etc.), line outlet wires with a cross-section of at least 2.5 mm², compliant with TS EN 60332-1-2, TS EN 60754-1/2 and TS EN 61034-2 standards, supply of all materials, delivery to the workplace and labour included. Measurement: Unit price no: 35.160.3400. Note: Conductors are colour-coded according to TS EN 60445 . Note: Manufactured in accordance with TS EN 50575 and TS EN 50575/A1 standards, the Construction Products Regulation 305/2011/EU, marketed with the CE conformity mark, and possessing the manufacturer's declaration of performance and a Certificate of Performance Constancy obtained from organisations accredited by the European Union.
Serial No. | 20
Item No. | 35.150.2197
Description | Installation of columns and supply lines with 4x35 mm² N2XH type 1KV underground cables
Unit | MT
Specification | Compliant with TS HD 604 S1 standard, N2XH, 0.6/1kV cables for installation within the building on plaster, on consoles or brackets to walls, ceilings or channels, and outside the building in channels, including the supply of underground cable at the workplace, passage and safety pipes, all types of material brackets and labour. Note: Manufactured in accordance with TS EN 50575 and TS EN 50575/A1 standards, the Construction Products Regulation 305/2011/EU, placed on the market with the CE conformity mark, and accompanied by the manufacturer's declaration of performance and a Certificate of Performance Constancy obtained from European Union accredited bodies.
Serial No. | 21
Item No. | 35.481.1340
Description | 4-output (quattro) LNB
Unit | AD
Specification | Input signal: 10.7 ~ 12.75 GHz, output signal: 950 ~ 2150 GHz bands, noise level > 0.6 dB, conversion gain > 65 dB, supply of the LNB device to the workplace, installation in accordance with the project and delivery in working order, including all materials and labour.
Serial No. | 22
Item No. | 35.481.1150
Description | 10/8 multiswitch
Unit | AD
Specification | Satellite (SAT) and terrestrial (TERR) inputs, with a maximum output power of at least 90 dBμV (satellite), featuring 100 V subscriber port protection, Allowing subscriber control via LED, Featuring a +4 dB equaliser on each subscriber output to compensate for excessive loss at high frequencies, With a maximum gain difference of +/- 3 dB between the first and last subscribers, SAT-SAT isolation > 40 dB, SAT-TERR isolation > 40 dB, RF connector is a 75 ohm F connector, capable of providing at least 47 mA Horizontal (H) and at least 32 mA Vertical (V) current for each subscriber output, supports DiSEqC 2.0-2.1 software, Features 4K, FullHD, DVB-S2, DVB-S, DVB-T2, DVB-T, DVB-C-HDTV, equipped with a port locking system, TERR frequency operating range 47 - 870 MHz, SAT frequency operating range 950 - 2150 MHz, Operates with an SMPS power supply adapter with an output range of 16V/1.5A ~18V/2A, Operating temperature range: -15...+50°C Supply of the multiswitch device to the workplace, installation in accordance with the project, and delivery in working order, including all materials and labour.
Serial No. | 23
Item No. | 35.505.1020
Description | RG6-U6 CABLE
Unit | MT
Specification | Radio, TV, Radar, Fire control, many transmitter devices, security satellite antennas, CCTV antennas and measurement systems, where signal loss must be kept to a minimum or external interference must be avoided. and bearing the CE conformity mark. This includes the supply of coaxial cable to the workplace, along with conduits, security pipes, and all materials and labour. Note: Includes internal installations (e.g., PEX, Bergman, or PVC pipes).
Serial No. | 24
Item No. | 35.505.1026
Description | RG11-U6 CABLE
Unit | MT
Specification | Radio, TV, Radar, Fire control, many transmitter devices, security satellite antennas, CCTV antennas and measurement systems, where signal loss must be kept to a minimum or external interference must be avoided. These cables are manufactured in accordance with the TS EN 50117-1 standard and the 2014/35/EU Directive on Electrical Equipment Designed for Use within Certain Voltage Limits, and bearing the CE conformity mark. This includes the supply of coaxial cable to the workplace, along with conduits, security pipes, and all materials and labour. Note: Includes internal installations (e.g., PEX, Bergman, or PVC pipes).
Serial No. | E-29
Item No. | 35.481.1400
Description | Satellite Socket
Unit | AD
Specification | Supply of satellite sockets with DC pass-through F connectors for the workplace, with a maximum output loss of 1.2 dB, including the case, installation in accordance with the project, and delivery in working order, including all materials and labour.
Serial No. | E-30
Item No. | 35.481.1210
Description | At least 90 cm offset dish antenna
Unit | AD
Specification | Electrostatic or polyester powder-coated antenna manufactured from at least 0.6 mm galvanised sheet metal, aluminium LNB arm and plastic LNB clamp, wall or floor mounting bracket, delivery to the workplace, installation in accordance with the project, and delivery in working order including all materials and labour.
Serial No. | 25
Item No. | 35.190.1704
Description | Data plug CAT 5e or CAT 6e RJ-45 (8-pin) (22.5 x 45 mm)
Unit | AD
Specification | Network and UPS earthed sockets comply with the TS IEC 60884-1+A1+A2 standard, socket holes normal or 45° angled, child-proof, IP 20 protection class, with a connecting bar between sockets for bar connection applications, Data sockets are RJ-45 type, supporting both T568A and T568B connection types, with spring-loaded dust protection covers, Telephone sockets RJ-11 or RJ-12 type, spring-loaded dust protection cover, with a transparent cover for labelling, flame-retardant (UL94 V0) material (claw or slide type) supply of sockets, delivery to the workplace, installation, cable connections, delivery in working order including all materials and labour. Socket installation kit and frame prices are included in the unit price.
Serial No. | 26
Item No. | 35.190.1703
Description | Telephone socket RJ-11 or RJ-12 (6-pin) (22.5 x 45 mm)
Unit | AD
Specification | Network and UPS earthed sockets comply with the TS IEC 60884-1+A1+A2 standard, socket holes are either standard or 45° angled, child-proof, IP 20 protection class, with a connecting bar between sockets for bar connection applications. Data sockets are RJ-45 type, supporting both T568A and T568B connection types, with spring-loaded dust protection covers. Telephone sockets are RJ-11 or RJ-12 type, with spring-loaded dust protection covers, featuring a transparent cover for labelling, and flame-retardant (UL94 V0) material (claw or rail type), delivery to the workplace, installation, cable connection, delivery in working order including all materials and labour. Socket installation kit and frame prices are included in the unit price.
Serial No. | 27
Item No. | 35.400.1010
Description | Wireless Transmitter Device
Unit | AD
Specification | It is a transmitter used to send messages to pager devices. It consists of a central unit and auxiliary antennas positioned at points where the signal weakens. Operating in the SBT (Industrial, Scientific, Medical) band defined in the KET (Short Range Radio) regulations, it transmits messages in accordance with the POCSAG standard, an international standard communication protocol, and can communicate with each other without the need for any data cabling structure. The coverage area can be simply expanded by placing a repeater near the coverage area boundary. cabling structure, and can simply extend the coverage area by placing a repeater near the coverage area boundary at a point without coverage. The device has a power supply of 220VAC or 12-24VDC. The supply, delivery to the workplace, installation, and connection of the device shall be delivered in working condition.
Serial No. | 28
Item No. | 35.540.4008
Description | Central Single-Tube 2-Fibre 1x2 9/125 SM Unarmoured LSOH Fibre Optic Cable
Unit | MT
Specification | Single mode (SM) fibre optic cables are used in wide area networks (WAN) and local area networks (LAN), closed-circuit television (CCTV) systems, industrial automation systems (SCADA), and cable TV systems for the transmission of high-quality voice, data, and images over long distances. The fibre core/strand diameter is 9/125 μm, and each strand is additionally wrapped in a 250-micron diameter sheath. The fibre core/cladding diameter is 9/125 μm, and each cladding is additionally wrapped in a 250-micron-diameter sheath. It is armoured with corrugated/grooved steel tape or unarmoured, with an LSOH outer sheath, filled with ‘Thixotropic gel’ to prevent water ingress. Maximum optical attenuation: 0.38 dB/km at 1310 nm, 0.25 dB/km at 1550 nm. Complies with TS EN 60332-1, TS EN 60793-1-1, TS EN 60794-1-23, TS EN 61034-1/2, TS EN 60754-1/2 standards. It is terminated only by the ‘fusion splice’ method using a special welding machine and is put into service after being tested end-to-end with an OTDR test device. Each fibre optic cable is tested with an OTDR device after installation and the test reports are submitted to the administration. All materials and labour are included. Each fibre optic cable shall be tested with an OTDR device after installation, and test reports shall be submitted to the administration. All materials and labour included. Note: Manufactured in accordance with TS EN 50575 and TS EN 50575/A1 standards and the 305/2011/EU Construction Products Regulation, marketed with the CE conformity mark, and possesses the manufacturer's declaration of performance and a Certificate of Constancy of Performance obtained from organisations accredited by the European Union.
Serial No. | 30
Item No. | 35.446.2140
Description | 48-Port Managed Network Switch, with at least 48 10/100/1000 Mbps Ethernet ports, at least 4 10 GB SFP ports
Unit | AD
Specification | The device must have a 220V AC operating voltage. In accordance with the Regulation on Electrical Equipment Designed for Use within Certain Voltage Limits 2014/35/EU in accordance with the regulation on Electrical Equipment Designed for Use with Specific Voltage Limits (2014/35/EU) and bearing the CE conformity mark. The device shall be delivered to the workplace, installed, and handed over in working order, including all necessary small installation materials. The switch shall have the number of ports specified on it.
Serial No. | 32
Item No. | 35.515.1002
Description | 2 x 2 x 0.8 + 0.8 mm2 J-H(St)H HALOGEN-FREE FIRE ALARM CABLES
Unit | MT
Specification | Used in security systems, communications, enclosed and dry areas, compliant with TS EN 60228, copper conductor, conforming to DIN VDE 0815; with an operating temperature range of -30°C to +70°C (for fixed installations), conforming to TS EN 50290-2-26, halogen-free flame-retardant, with stranded insulation, twisted strands, and aluminium foil wrapped with an earth wire, outer sheath RAL 7032 grey, compliant with TS 13767 standard, halogen-free flame-retardant, compliant with TS EN 50290-2-27, supply of insulated fire alarm cable, conduits and safety pipes, all materials and labour included. Note: HFFR pipe is included in internal installations. Note: Manufactured in accordance with TS EN 50575 and TS EN 50575/A1 standards, the Construction Products Regulation 305/2011/EU, marketed with the CE conformity mark, and possessing the manufacturer's declaration of performance and a Certificate of Constancy of Performance obtained from organisations accredited by the European Union.
Serial No. | 33
Item No. | 35.515.2090
Description | 3x1.5 mm² LIH(St)H Halogen-Free Signal and Control Cable
Unit | MT
Specification | These halogen-free, shielded control and internal connection cables are used in electronic control systems, in all communication systems for audio frequency transmission, in electronic information communication, and in industrial electronics. It consists of flexible cables with multiple twisted tinned copper conductors, insulated with halogen-free flame-retardant material in colours compliant with DIN 47100 colours compliant with the DIN 47100 standard, and the strands are twisted together in layers to form a cable (with an operating temperature range of -30°C to +70°C) with an earth wire, shielded with AL-PES wrapping tape, with a flame-retardant HFFR compound outer sheath in RAL 7001 grey, compliant with TS 13755 standard, IEC-332-1, IEC-332-3, IEC-60754, IEC-60332 flame test certificate, compliant with TS EN 60332-1-2, TS EN 60754-1 and TS EN 61034-2 standards, supply of signal and control cables to the workplace, including passage and safety pipes, all types of materials and labour included. Note: Manufactured in accordance with TS EN 50575 and TS EN 50575/A1 standards, the Construction Products Regulation 305/2011/EU, marketed with the CE conformity mark, and possessing the manufacturer's declaration of performance and a Certificate of Constancy of Performance obtained from organisations accredited by the European Union.
Serial No. | E-31
Item No. | 35.410.2020
Description | Addressable optical smoke detector
Unit | AD
Specification | The microprocessor-controlled detector must have a photoelectric smoke cell that operates on the light scattering principle. The detector must have at least one LED light to enable remote visual control. It must have a socket suitable for parallel alarm lamp connection and allow for easy installation and removal. Detector addressing must be possible automatically via any position key, handheld detector programming device, or fire detection and alarm control panel. The detector must be manufactured in accordance with the TS EN 54-7 standard, the 305/2011/EU Construction Products Regulation, must be placed on the market with a CE conformity mark, and must possess the manufacturer's performance declaration and a Performance Consistency Certificate obtained from organisations accredited by the European Union. The supply of the detector, its delivery to the workplace, including all small materials, and its delivery in a tested and operational state.
Serial No. | E-32
Item No. | 35.410.2540
Description | Addressable resettable fire alarm button
Unit | AD
Specification | The addressable resettable fire alarm button will function as a manual call point in the system and will be suitable for surface and flush mounting and microprocessor controlled. It should be activated by pressing the flexible, unbreakable glass on its surface and should remain in this state until the reset operation is performed. The LED on the fire alarm button will flash when the button is queried by the control panel via the circuit, and will remain lit continuously when manually activated to trigger the alarm. The button shall be weatherproof and have a protection rating of at least IP 65. It shall be manufactured in accordance with the TS EN 54-11 standard and the 305/2011/EU Construction Products Regulation, marketed with the CE conformity mark, and accompanied by the manufacturer's performance declaration and a Performance Constancy Certificate from bodies accredited by the European Union. The supply of the button, its delivery to the workplace including all small materials, and its delivery in a tested and operational state.
Serial No. | E-33
Item No. | 35.410.3030
Description | Addressable short-circuit isolator-equipped, circuit-powered, flashing fire alarm siren
Unit | AD
Specification | Addressable short-circuit loop-powered flashing fire alarm siren on the loop circuit will have an internal short-circuit isolator to ensure the system continues to operate in the event of a short circuit on the circuit. The module is manufactured in accordance with TS EN 54-3, TS EN 54-23 and TS EN 54-17 standards, the 305/2011/EU Construction Products Regulation, and is placed on the market with the CE conformity mark and comes with the manufacturer's performance declaration and a Performance Consistency Certificate obtained from organisations accredited by the European Union. The supply of the module, which is identical in all other respects to the unit price number 35.410.3020, including delivery to the workplace and all small materials, and delivery in a tested and operational state.